## Slide 1
Marsili RT (ed.) (2001) Flavor, Fragrance and Odor Analysis. New York: Marcel Dekker.
Mistry BS, Reineccius T and Olson LK (1997). Gas chromatography-olfactometry for the determination of
key odorants in foods. In: Marsili RT (ed.) Techniques for Analyzing Food Aroma, pp. 265-292. New York: Marcel Dekker.
Moio L, Langlois D, Etievant P and Francesco A (1993). Powerful odorants in bovine, ovine, caprine and water buffalo milk by means of gas chromatography- olfactometry. Journal of Dairy Research 60: 215-222.
Ott A, Fay LB and Chaintreau A (1997). Determination and origin of the aroma impact compounds of yoghurt flavor. Journal of Agricultural and Food Chemistry 45: 850-858.
Roberts DD, Pollien P and Milo C (2000). Solid-phase microextraction method development for headspace analysis of volatile flavor compounds. Journal of Agricultual and Food Chemistry 48: 2430-2437.
Shipe WP, Bassette R, Deane DD et al. (1978) Off flavours of milk: nomenclature, standards, and bibliography.
Journal of Dairy Science 61: 855-869.
FLOW EQUIPMENT
Principles of Pump and Piping Calculations
J C Oliveira, University College, Cork, Ireland
Copyright 2002, Elsevier Science Ltd. All Rights Reserved
Introduction
Promoting and controlling the flow of liquids re- quires an understanding of the relationship between pressures and flow rates, which is reviewed in this article. The factors that are characteristic of the li- quid or that depend on the installation or piece of equipment where such flow occurs are analysed. The basic principles that govern the calculations required to select pumps, valves and design installations are thus understood in fundamental terms.
Principles of Calculation
Ideal Flow
Conservation of mechanical energy
The basic prin-
ciple used to describe the flow of liquids in any type
of installation is that the total mechanical energy of an element of the fluid at a given position, A, should be maintained while it flows, so that when it reaches another position, B, there may have been conversion of one form of energy to another, but the total should be the same. This analysis is applied at isothermal conditions, so that only mechanical energy needs to be considered (nonisothermal flow will not be addressed).
Three forms of energy are involved: pressure, potential energy and kinetic energy. The mathemat- ical expression that translates this principle of conservation of mechanical energy is known as Ber- noulli's equation (the differential form is Euler's equation), and for isothermal ideal flow of incom- pressible fluids (liquids), it can be written as:
Pa
p · g 2g p · g
+ ha + a
v2 v2
Pb
+ hb +
b
2g
[1]
where P is pressure, h the height (vertical distance from the ground to the central axis of the pipe), v the average velocity and the subscripts a and b designate the values at locations A and B, respectively. p is the specific gravity of the liquid and g the acceleration due to gravity (9.8 m2 s-1). The left-hand side is the
Contents
Principles of Pump and Piping Calculations Pumps
Valves
FLOW EQUIPMENT/Principles of Pump and Piping Calculations 1081

## Slide 2
sum of energy terms at location A, and the right- hand side at location B. This equation is written so that all terms have units of length (e.g. m), and are known as 'heads': the first term is the pressure head, the second is the potential head and the third is the kinetic head. Figure 1 sketches a generic situation where all heads have changed from location A to B, in an example where the potential and kinetic heads have increased at the expense of the pressure head.
Conservation of momentum In addition to Ber- noulli's equation, it can also be stated that there should be a conservation of momentum. For steady flow, this principle reduces to a mathematical ex- pression which simply states that the flow rate must be constant throughout the installation, otherwise there would be an accumulation of liquid. For incompressible fluids, the volumetric flow rate (Q) is used, which is equal to the average velocity of the fluid times the cross-sectional area of the pipe (A), and this leads to the so-called continuity equation:
va · Aa vb · Ab [2]
General design principles Substituting eqn [2] in eqn [1] and with some basic manipulation, the expression that relates flow rate to the pressure dif- ference between two locations (which is designated 8.P) is obtained:
8. P Q 1
p · g 8. + 2g
h
2 ( \
A2 - A2
a
1
b
[3]
where 8.P Pa - Pb; 8.h hb - ha. It should be noted that, by definition, Q Va · Aa (or Q Vb · Ab) and that for cylindrical pipes (circular cross-section area), A (1r · D2)/4, D being the diameter of the pipe.
Equation [3] allows calculation of the pressure difference that must exist to ensure a given flow rate,
or by reversing it, to calculate the flow rate that a given pressure difference will imply.
Nonideal Flow
Head losses The analysis above implies that the fluid behaves ideally, i.e. there is no dissipation of mechanical energy. However, this is rarely true and fluids exhibit a resistance to flow which depends on their rheological properties. The concept of viscosity is familiar - a viscous fluid shows greater resistance to flow. Fluids are not rigidly structured materials and flow implies a continuous movement of mol- ecules in relation to one another. Either through viscous shear energy dissipation or by molecular collisions, there is inevitably a loss of mechanical energy, dissipated in the form of heat. It is assumed that this is not so significant that the situation will cease to be isothermal - it is considered that the heat dissipated is transferred easily and lost to the outside and causes no significant rise in temperature. However, while flowing from A to B, part of the mechanical energy is lost. Equation [1] is therefore incorrect, and a term (FA --- B) must be inserted to account for all head losses:
Pa va
p · g + a + 2g p · g + b + 2g +
h h F 4
2 2
Pb
vb
A---B
[ ]
Hence, the problem can be solved in the same way as if the fluid was ideal, with a minor correction to eqn [3]:
8. P
p · g
FA---B + 8.h
+ 2g
Q 1
2
A2 - A2
b
1
a
( \
[5]
To deal with this new factor, it is necessary to know more about fluids and their flow behaviour.
Viscosity and flow regimes Reynolds performed a simple experiment to visualize how fluid molecules move in the flow of liquids. He injected a dye at a given point in a transparent tube section and noted how the colour dispersed in the flow (Figure 2). He found that, for low flow rates, a smooth straight line developed. At different distances from the pipe wall, the velocity of this line was different. He concluded that, at low flow rates, the molecules move in layers and there is no collision between them, but there is friction between adjacent layers, as they move at different velocities (maximum at the centre of the tube, and approaching zero near the walls). He des- ignated this situation as laminar flow.
However, when the flow rate is increased, a critical point is reached where turbulence starts to develop and the dye moves unpredictably along the tube. In this case, it is evident that there will be collisions
A
P = 5.0  10 Pa
h = 0 m v = 1.0 m s–1
5
P = 4.73  105 Pa
h = 2.0 m v = 4.0 m s–1
B
Figure 1 Conservation of mechanical energy in an ideal system.
1082 FLOW EQUIPMENT/Principles of Pump and Piping Calculations

## Slide 3
between the molecules and the flow is turbulent. Figure 2 shows how a single drop of dye solution might move along the tube - different drops will move along different paths, as turbulent patterns are unstable (time-dependent).
Figure 3 helps to visualize two layers of molecules moving adjacent to each other and at different vel- ocities. Newton's law states that the shear stress (the force per unit cross-sectional area exerted tangen- tially to the layers, which is responsible for the ve- locity difference) should be proportional to the shear rate (the variation of the velocity per unit length), and that proportionality is the viscosity. Hence:
dv
(} µ dy
[6]
where (} is the shear stress, µ the viscosity, dv/dy the shear rate, v the velocity and y the height.
However, not all fluids obey this law, and those that do not are termed non-Newtonian. Water and milk are Newtonian fluids, while most viscous li- quids are non-Newtonian.
It makes sense to think that the head losses due to viscous shear energy dissipation in laminar flow,
where there are no collisions, should be proportional to the viscosity. This result has been verified em-
pirically and later derived theoretically. The so-called Hagen-Poiseuille equation can be written as:
F p D2 µ
32 · L · v
g ·
[7]
where L is the length of pipe (distance from A to B) and v is the average velocity (it should be noted that the velocity of a specific layer varies with the distance from the wall), which is given simply by dividing the flow rate by the cross-sectional area.
On the other hand, when there is fully turbulent flow, with collisions between molecules causing the loss of so much energy that the effect of viscosity is irrelevant, the head losses should be proportional to the kinetic head. The so-called Darcy-Weisbach equation is applied in this case, stating that:
L v2 F f D 2g
[8]
where f is a friction factor that depends on the roughness of the pipe.
It has been found that the critical point when laminar flow ceases and eqn [7] is no longer valid occurs for all systems when the so-called Reynolds number reaches a value of 2000. The Reynolds number is the ratio between kinetic and viscous forces, and its application is based on the principle of dynamic similarity. It is:
Re
p · v · D
µ
[9]
Note from eqns [7], [8] and [9] that it can be con- cluded that the Darcy-Weisbach equation can be used in laminar flow, provided f is considered as a value which varies with the Reynolds number, with f 64/Re.
However, once laminar flow ceases, fully turbulent flow is not immediately established, where viscosity is irrelevant and eqn [8] applies. Between Re 2000 and 4000 there is an instability regime, where the flow can switch from laminar to turbulent, and above that there is a gradual change to fully turbulent flow as Re increases. This is well visualized by plotting the f value of the Darcy-Weisbach equation as a function of the Reynolds number, in what is known as the Moody diagram (Figure 4). In laminar flow, there is a
y2 y1
v1
v2
y2 – y1
v = dv
y dy
lim
y 
Figure 3 Concept of viscosity as friction between adjacent layers of fluid moving at different velocities.
FLOW EQUIPMENT/Principles of Pump and Piping Calculations 1083
Injection of dye at h2
Injection of dye at h1
Low flow rate – laminar flow
Figure 2 Reynolds's experiment and concepts of laminar and turbulent flow.
High flow rate – turbulent flow
h2 h1
v2 – v1
v
=
y

## Slide 4
straight line in a log-log graph (f 64/Re). In fully developed turbulent flow, f is constant, and in between there are the instability and the transition regimes. The point at which fully turbulent flow is reached and f is constant depends on the roughness of the pipe wall. For very smooth tubes, which is the case of stainless steel pipes used in the hygienic design of food-processing installations, fully tur- bulent flow is not actually reached in regions of practical interest of Re. In transition flow, the Colebrook-White empirical equation can be used to estimate f:
1 k 2.51
../-f- -2 · log
3.7D + Re
f
../---
( \
[10]
where k is the roughness factor of the pipe (for smooth tubes, k 0) and log is the decimal logarithmic.
Viscous shear energy dissipation The effect of vis- cous shear energy dissipation and of collisions between molecules during flow due to turbulence are calculated using eqn [8], with f being given by eqn [10]. However, as this is an implicit equation for f, many people prefer to read the result graph- ically from Moody's diagram; a simple version is given in Figure 4.
Localized head losses It is evident that any geo- metric variation in the installation, such as bends, junctions and expansions, will cause collisions between molecules and the pipe walls, and between
molecules themselves, resulting in turbulence. Whether the flow regime is laminar or turbulent prior to these geometric effects, there are kinetic losses due to collisions, and hence it is reasonable to assume that these head losses should be proportional to the kinetic head. The simple expression used is similar to eqn [8], but there is no need to individualize the length and diameter of these elements, and a simpler expression can be used:
v2 F K 2g
[11]
where K, the so-called 'number of velocity head losses', must be estimated depending on the con- striction. Various tables and graphs to estimate K for the various relevant elements that may exist in an installation can be found in the literature, such as bends (where K depends on the curvature), expan- sions and contractions (where K depends on whether the expansion/contraction is sudden or gradual and on the diameter before and after the element), junc- tions and flow dividers (where K depends on the type of junction), and valves (where K depends on the type of valve). Except at low Reynolds numbers in some cases, K is usually independent of Re, just like f in fully turbulent flow.
Calculation of head losses in an installation When calculating the head losses in an installation, eqn [5] is applied and FA --- B estimated as the sum of all individual head losses: in each straight section of the pipes there is viscous shear energy dissipation given
0.02
Smooth tubes (k = 0)
0.01
103 104 105
106
Re
L 0.10
0.09
0.08
0.07
0.06
0.05
f = 64/Re
0.04
f
0.03
k /D = 0.01
k /D = 0.002
Figure 4 Moody's diagram (plots of eqn [10] for transition and turbulent regimes).
1084 FLOW EQUIPMENT/Principles of Pump and Piping Calculations
Instability
aminar |  | Transition Fully turbulent |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 

## Slide 5
by eqn [8], and in each element that can cause localized head losses, eqn [11] is used with the corresponding K-value.
Net Positive Suction Head
Cavitation
When point B is located above point A, and with the added effect of head losses contributing to pressure decrease, Bernoulli's equation indicates that it is eventually possible to reach a pressure low enough to be at the boiling point of the liquid. This would result in the release of gas bubbles. From Bernoulli's equation, the points to check will be those with smaller cross-sectional area (higher velocity) and located higher in the installation. Gas bubbles are difficult to move, and this could result in severe loss of pumping efficiency. Moreover, the impact of gas bubbles collapsing against a surface moving at high speed is very destructive for centrifugal pumps (cavitation). Hence, the situation where point B is the entrance of a pump is of particular concern (Figure 5).
Available Net Positive Suction Head
The net positive suction head (NPSH) in a given point is defined as the pressure head above the vapour pressure head, that is:
NPSH p g -
P
Pv
p · g
[12]
where P is the pressure of the liquid at that point and Pv is the vapour pressure (pressure at which the liquid is boiling for the system temperature - for
instance, the vapour pressure of water at 100 oC is 1 atm, at 20 oC it is 0.025 atm).
The NPSH available (NPSHa) is the value of the NPSH at the entrance of the pump. It can be calcu- lated by determining the pressure at point B from eqn [3], knowing the pressure at point A, and estimating all relevant head losses using the appro- priate eqns [8] and [11]. Mathematically:
NPSHa - 8.h - FA---B
Pa
p · g
Q2 ( 1
- 2g
A2 - A2
b
1 \
a
Pv
- p · g
[13]
It is noted that if the cross-flow areas at A and B are the same, the kinetic flow rate term is zero.
Required Net Positive Suction Head
In principle, there would be no cavitation if NPSHa is greater than zero. However, in every pump there will be head losses until the fluid starts to build up pressure - there are possibly geometric constrictions at the entrance, collisions with pump parts, etc. Usually, pump manufacturers will provide this information in terms of a NPSH required (NPSHr), from bench scale tests. Basically, these are the head losses that occur at the pump entrance, until the li- quid builds up pressure. Thus, the NPSHr of the pump (or pumps being analysed) must be checked to ensure that NPSHa>NPSHr. A safety margin of about 0.7-1 m is normally recommended.
It is noted that the NPSHr, like all head losses, is obviously a function of the flow rate, and pump manuals usually provide the NPSHr in the form of a graph, as a function of the flow rate or of the Reynolds number.
Pumping Efficiency and Power Requirements
Calculation of Pumping Requirements
Generically, a pump will be located somewhere between the entrance of an installation (piping line, piece of equipment) and the exit, and must promote a given flow rate. Applying Bernoulli's equation between the exit of the pump and the exit of the installation gives the pressure head that must exist at the pump exit to ensure the flow rate specified:
He p g + 8.h + Fe---out +
Pe
p · g
Pout
Q2 1
2g
A2 A2
out e
[14]
-
1 \
A
B
Liquid
Reservoir/feed tank
Pump
Figure 5 Pump in suction mode from lower reservoir.
FLOW EQUIPMENT/Principles of Pump and Piping Calculations 1085

## Slide 6
where He is the pressure head at the exit of the pump, and the subscripts e and out indicate values at the exit of the pump and at the end of the installation, respectively. Fe --- out is the total head loss from the pump onwards.
Similarly, the pressure head at the pump inlet can be calculated by applying Bernoulli's equation be- tween the entrance of the installation and the pump:
Hi p.g p.g - 8.h - Fin---i - 2g
Pin
Pi Q2 1 1 \
A2 - A2
in i
[15]
Power, Energy and Calculation of Pumping Costs
Assuming the usual case of no variation in the potential and kinetic heads at the inlet and outlet of the pump (same cross-flow area and level height), the power provided by the pump to the liquid (W, energy per unit time) to ensure the flow rate, Q, is that re- quired to raise the pressure head from Hi to He:
W p · g · Q · (He - Hi) [16]
To calculate the pumping energy costs, it must be noted that not all power used by the pump from the mains electrical supply will be delivered to the fluid, as there are various energy losses. The pump effi- ciency ('T) is the ratio between the power delivered to the fluid (W) and that spent from the mains (Wused):
'T W
W
used
[17]
The pump efficiency depends on the type of pump and on the conditions of operation. Generally, there is an optimum efficiency for a given flow rate - operating above or below implies that the pump is under- or overdimensioned for the job, and the consequence is that the pumping efficiency is lower. Hence, engineers must select the pump dimensions according to the specific job, targeting the region of operation of the pump where 'T is maximum, as
otherwise
Wused,
and hence pumping costs, are
higher than they could be with an appropriate pump. They may also find that using more than one pump in parallel lines may be more efficient than a single, larger pump. Optimum efficiencies for centrifugal pumps are of the order of 80-90%. This subject is discussed in more detail elsewhere (see Flow Equip- ment: Pumps).
Pressure Drop in Valves
In a certain way, valves are the opposite of pumps. They are the elements that cause a loss of pressure
head. From eqn [14], as a valve increases, the head losses, Q, decrease. The head loss caused by a valve is generally described by eqn [11]. The value of K will depend on the type of valve and percentage opening, and is given by manufacturers (otherwise, estimates can be found in the literature for generic valves). Valves and pumps work together: pumps must have some overcapacity and have a valve next to it (the discharge valve) to control the pressure to the desired level. Otherwise, the flow would be subjected to fluctuations due to variations in atmospheric pres- sure and temperature. Discharge valves and surge valves may also be needed for start-up and/or shut- down procedures.
Care should be taken to ensure that the pressure head at the exit of the valve when it is in the lowest opening position (higher K) does not go below the vapour pressure, which can be checked with Ber- noulli's equation, in a similar manner to NPSHa calculations.
See also: Flow Equipment: Pumps; Valves. Heat Exchangers. Pasteurization of Liquid Milk Products: Pasteurizers, Design and Operation. Process and Plant Design.
Further Reading
Chhabra RP and Richardson JF (1999) Non-Newtonian Flow in the Process Industries. Oxford: Butterworth- Heinemann.
Evett JB and Liu C (1989) 2500 Solved Problems in
Fluid Mechanics and Hydraulics. New York: McGraw- Hill.
Evett JB, Liu C and Giles RV (1995) Schaum's Interactive Outline of Fluid Mechanics and Hydraulics. New York:
McGraw-Hill.
Foust AS, Wenzel LA, Clump CW, Maus L and Andersen LB (1980) Principles of Unit Operations, 2nd edn.
New York: John Wiley.
Granger RA (1995) Fluid Mechanics. New York: Dover.
Mott RL (2000) Applied Fluid Mechanics, 5th edn. New York: Prentice-Hall.
Perry R and Chilton C (1984) Perry's Chemical Engineers' Handbook, 6th edn. New York: McGraw-Hill.
Rao MA and Rizvi SSH (1995) Engineering Properties of Foods, 2nd edn. New York: Marcel Dekker.
Roberson JA and Crowe CT (1996) Engineering Fluid Mechanics, 6th edn. New York: John Wiley.
Streeter VL, Wylie EB and Bedford KW (1998) Fluid
Mechanics, 9th edn. New York: McGraw-Hill.
White FM (1998) Fluid Mechanics, 4th edn. New York: McGraw-Hill.
1086 FLOW EQUIPMENT/Principles of Pump and Piping Calculations