| Duct Sizing Table |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  | 11 | 12 |
| Section | Length (m) | Flow Rate (m3/s) | Pressure drop per metre (Pa/m) | Duct Size (mm) | Velocity (m/s) | Velocity Pressure (Pa) | Fittings pressure loss factor or  (zeta) factor | Pressure Loss |  |  | Total Pressure Loss (Pa) | Cumulative Pressure Loss (Pa) |
|  |  |  |  |  |  |  |  | Fittings (Pa) |  | Straight Duct (Pa) |  |  |
| A | 10 | 1.2 | 1.0 | 0.47 m dia. (0.47/2)2 / 0.350 = 0.4957 500 x 350mm | 1.2 / (0.5 x 0.35) = 6.86 | 0.5 x 1.2 x 6.862 = 28.2 | Intake louvre = 6.5 Bend = 0.67 Reduction to section B will go in downstream section (B). TOTAL = 7.17 | 28.2 x 7.17 =202 |  | - x 10 = 10 | 202 + 10 = 212 | 212 |
| B | 3 | 0.9 | 1.0 | 0.43 m dia. 425 x 350mm | 6.05 | 22.0 | Branch Index Circuit is straight through (VP1 to VP2) . The VP ratio VP2/VP1 = 22 / 28.2 = 0.78 The zeta factor from EXAMPLES OF zeta FACTORS is 0.09 Reduction  = 0.2 for taper on one side. TOTAL = 0.29 | 0.29 x 22 = 6 |  | 3 | 9 | 221 |
| C | 6 | 0.6 | 1.0 | 0.37 m dia. 325 x 350mm | 5.28 | 16.7 | Branch VP ratio = 16.7 / 22 = 0.76 zeta factor = 0.16 by interpolation Reduction  = 0.2 for taper on one side. TOTAL = 0.36 | 6 |  | 6 | 12 | 233 |
| D | 8 | 0.3 | 1.0 | 0.28 m dia. 175 x 350mm | 4.90 | 14.4 | Branch VP ratio = 14.4 / 16.7 = 0.86 zeta factor = 0.08 by interpolation Reduction  = 0.2 for taper on one side. Bend = 0.67 Outlet diffuser = 3.5 TOTAL = 4.45 | 64 |  | 8 | 72 | 305 |